{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["LHV HHV"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"LHV HHV","index":0,"n_rows":33,"n_cols":15,"rows_kept":33,"cut":false,"hidden":false,"merged":[]}
[]
[null,null,null,"Fuel",null,{"$f":"_xll.alera(\"TX0218FUEL06\",E4,E6,E9,E10,E11,E13,E14,E15,E16)","v":"Link"},"as rec.",null,null,null,null,null,"Comb.",null,{"$f":"_xll.alera(\"TX0218COMB02\",N6,N16,N18,N19,N20,N22,N21,,,,,,,,,M25,M26)","v":"Link"}]
[null,null,null,"F00010005",null,null,"IN WET"]
[null,null,null,"H2O",8.16,"%",{"$f":"E4","v":8.16},null,null,null,null,null,"Heat",0.37222406388714957,{"$f":"_xll.aleraTX(\"TX0554TXCOMBX1\")","v":"MW net"}]
[null,null,null,null,null,null,null,null,null,null,null,null,"Exit gas",1186.896053027662,"°C"]
[null,null,null,"LCV",13.288384000000001,{"$f":"_xll.aleraTX(\"TX0550TXFUELBX\")","v":"MJ/kg"},null,null,null,null,null,null,null,null,13.288384000000001]
[null,null,null,"G 6",14.732128610800006,"MJ/kg",null,null,null,"Nm3/h H2O",{"$f":"N7*N12/100","v":87.727960199004968},null,"gas",647.00809645811819,"Nm3/h"]
[null,null,null,"dry",null,null,null,null,null,"kg/h H2O",{"$f":"K7*0.804","v":70.533280000000005},null,null,829.82122414562366,"kg/h"]
[null,null,null,"C",40.722996515679455,"%",{"$f":"E9*(100-$E$4)/100","v":37.400000000000013},null,null,"kg H2O / kg Fuel",{"$f":"K8/N21","v":0.70533280000000009},null,null,"Vol(wet) %"]
[null,null,null,"H",7.6001742160278765,"%",{"$f":"E10*(100-$E$4)/100","v":6.9800000000000022},null,null,null,null,null,"N2",69.663643673813112]
[null,null,null,"N",0.43554006968641112,"%",{"$f":"E11*(100-$E$4)/100","v":0.4},null,null,null,null,null,"CO2",10.715913432302319]
[null,null,null,"O",44.000435540069674,"%",40.409999999999989,null,null,null,null,null,"H2O",13.559020463460882]
[null,null,null,"S",0.10888501742160278,"%",0.1,null,null,null,null,null,"O2",6.0508685675577381]
[null,null,null,"ash",7.1319686411149821,"%",6.55,null,null,null,null,null,"SO2",1.0553862865939546E-2]
[null,null,null,"Cl",0,"%",0,null,null,null,null,null,"HCl",0]
[null,null,null,"F",0,"%",0,null,null,null,null,null,"O2 (dry)",7,"%"]
[null,null,null,"O/C",1.0804812834224593,"(mass)",null,null,null,null,null,null,"Air",569.95790097054442,"Nm3/h"]
[null,null,null,"H/C",0.18663101604278073,"(mass)",null,null,null,null,null,null,"base",15,"°C"]
[null,null,null,null,null,null,null,null,null,null,null,null,"heated",15,"°C"]
[null,null,null,null,null,null,{"$f":"SUM(G4:G19)","v":100},null,null,null,"atomic mass",null,"H2O",0,"g/kg"]
[null,"HHV 1",null,null,null,null,null,null,null,"H",1.0078400000000001,null,"Fuel",100,"kg/h"]
[null,"HHV = LHV +µ(H2O) * 2,4425 [MJ/kg]",null,null,null,"H2O from fuel moisture",{"$f":"E4/100","v":8.1600000000000006E-2},"kg/kg fuel",null,"O",15.9994,null,"Loss",0,"%"]
[null,"µ(H2O) kg H2O / kg Fuel in Flue Gas",null,null,null,"H2O from H2",{"$f":"G10*K24/100","v":0.62383542228925248},"kg/kg fuel",null,null,{"$f":"2*K21+K22","v":18.015080000000001}]
[null,"resulting from H2 and H2O in Fuel",null,null,null,"Total",{"$f":"G22+G23","v":0.70543542228925249},"kg/kg fuel",null,"H to H2O",{"$f":"K23/(2*K21)","v":8.9374702333703766},null,null,"Link to R - Gas"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Extra gas"]
[null,null,"kg H2O in Flue / kg Fuel",null,null,null,"Error",null,null,null,null,null,{"$f":"F2","v":"Link"},"Link to Fuel"]
[null,"Elementary Analysis of Fuel",{"$f":"G24","v":0.70543542228925249},{"$f":"E7+C27*2.4425","v":16.455154629741504},"HHV [MJ/kg]"]
[null,"aleraSoft Excel AddIn",{"$f":"K9","v":0.70533280000000009},{"$f":"E7+C28*2.4425","v":16.454903974800004},"HHV [MJ/kg]"]
[null,"Internet",null,{"$f":"E7+(0.212*G10+0.0245*G4+0.008*G12)","v":16.735088610800005},"HHV [MJ/kg]",null,{"$f":"(D29-D28)/D28","v":1.7027424555566679E-2}]
[]
[null,"Internet HHV 2"]
[null,"HHV = LHV +(0,212*H+0,0245*H2O+0,008 *O)"]
[null,"https://www.cement-co2-protocol.org/en/Content/Internet_Manual/tasks/lower_and_higher_heating_values.htm"]